## Description
Validation Testing Description
Test Number | Network File | Branch | Description
1 | Network_3_1_plant | i1031 | Comparison of timing and output values to master
2 | Network_3_1_plant | master | Comparison of timing and output values to master
3 | Network_3_2_plants | i1031 | Comparison of timing and output values to master
4 | Network_3_2_plants | master | Comparison of timing and output values to master
5 | Network_1_1_plant | i1031 | Funcionality test, timing test
6 | Network_1_2_plants | i1031 | Funcionality test, timing test
7 | Network_2_1_plant | i1031 | Funcionality test, timing test
8 | Network_2_2_plants | i1031 | Funcionality test, timing test

## Master_Comparison
Comparison of branched network solution of Master and Branch code
Network 3_1P
| Mass flow total [kg] | Heat loss total [kW] | Pressure loss total [Pa] | Heat supply total [kW]
Master | 47343.171 | 40733.495 | 561243394.51 | 2049416.961
Branch | 47343.171 | 40733.495 | 561243394.51 | 2049416.961
Difference Relative | 0% | 0% | 0% | 0%
Network 3_2P
| Mass flow total [kg] | Heat loss total [kW] | Pressure loss total [Pa] | Heat supply total [kW]
Master | 40670 | 41523 | 669486823 | 1580685
Branch | 40654 | 41540 | 668982714 | 1580744
Difference Relative | 0.04% | -0.04% | 0.08% | 0%

## Matlab_Comparison
Matlab validation of Kirchoff 1st and 2nd laws of calculated mass flows in matlab
Maximum Deviation from expected values
| Network 1_1P | Network 1_2P | Network 2_1P | Network 2_2P
Kirchoff 1st law | 1e-05 | 1e-05 | 3.5527e-15 | 1e-05
Kirchhoff 2nd law | 7.276e-07 | 6.5484e-11 | 5.8208e-11 | 5.8208e-11

## EPANET_Comparison
Comparison of CEA calculated mass flows for looped and mixed networks to EPANET calculations
Network 1_1P
[13 empty] | PLANT |  | Deviation relative to total demand
Timestep |  | PIPE0 | PIPE1 | PIPE2 | PIPE3 | PIPE4 | PIPE5 | PIPE6 | PIPE7 | PIPE8 | PIPE9 | PIPE10 | PIPE11 |  | PIPE 9
62 | CEA | 3.5077 | 0.32013 | 2.0316 | 1.9122 | 3.6237 | 5.3351 | 12.6905 | 6.2188 | 4.7602 | 0.11931 | 2.9295 | 18.0256
| EPANET | 3.54 | 0.31 | 2.02 | 1.84 | 3.55 | 5.27 | 12.76 | 6.25 | 4.8 | 0.18 | 2.91 | 18.03
| Absolute Difference | 0.03226 | -0.01013 | -0.01155 | -0.07223 | -0.07365 | -0.06507 | 0.0695 | 0.03115 | 0.03979 | 0.06069 | -0.01947 | 0.00443
| Relative Difference | 0.9113% | -3.268% | -0.5718% | -3.926% | -2.075% | -1.235% | 0.5447% | 0.4984% | 0.829% | 33.72% | -0.6691% | 0.02457% |  | 0.3366%
2172 | CEA | 0.99345 | 0.15937 | 0.54563 | 0.5134 | 0.89966 | 1.2859 | 3.2289 | 1.5851 | 1.2575 | 0.03223 | 0.83899 | 4.5148
| EPANET | 1.01 | 0.15 | 0.54 | 0.51 | 0.91 | 1.3 | 3.32 | 1.64 | 1.28 | 0.04 | 0.84 | 4.62
| Absolute Difference | 0.01655 | -0.00937 | -0.00563 | -0.0034 | 0.01034 | 0.01409 | 0.09113 | 0.05486 | 0.02252 | 0.00777 | 0.00101 | 0.10521
| Relative Difference | 1.639% | -6.247% | -1.043% | -0.6667% | 1.136% | 1.084% | 2.745% | 3.345% | 1.759% | 19.42% | 0.1202% | 2.277% |  | 0.1682%
8295 | CEA | 3.6164 | 0.2499 | 2.2818 | 2.1973 | 4.2292 | 6.261 | 15.5759 | 8.2316 | 5.3124 | 0.08444 | 3.1961 | 21.8369
| EPANET | 3.66 | 0.22 | 2.25 | 2.12 | 4.15 | 6.18 | 15.66 | 8.27 | 5.35 | 0.14 | 3.18 | 21.84
| Absolute Difference | 0.04358 | -0.0299 | -0.03175 | -0.07732 | -0.07916 | -0.08101 | 0.08413 | 0.03837 | 0.03758 | 0.05556 | -0.01611 | 0.00312
| Relative Difference | 1.191% | -13.59% | -1.411% | -3.647% | -1.907% | -1.311% | 0.5372% | 0.464% | 0.7024% | 39.69% | -0.5066% | 0.01429% |  | 0.2544%
Network 1_2P
|  | PLANT PIPE11: PLANT | PLANT
Timestep |  | PIPE0 | PIPE1 | PIPE2 | PIPE3 | PIPE4 | PIPE5 | PIPE6 | PIPE7 | PIPE8 | PIPE9 | PIPE10 | PIPE11 | PIPE12 |  | PIPE 7
55 | CEA | 9.9222 | 5.2374 | 1.8454 | 2.2656 | 4.2963 | 4.2963 | 5.9269 | 0.301 | 4.1972 | 1.6104 | 0.5561 | 10.2232 | 10.2232
| EPANET | 10.05 | 5.32 | 1.76 | 2.23 | 4.26 | 4.26 | 5.97 | 0.17 | 4.11 | 1.56 | 0.52 | 10.22 | 10.22
| Absolute Difference | 0.12783 | 0.0826 | -0.08539 | -0.03564 | -0.03631 | -0.03631 | 0.04314 | -0.131 | -0.08719 | -0.05043 | -0.0361 | -0.00317 | -0.00317
| Relative Difference | 1.272% | 1.553% | -4.852% | -1.598% | -0.8523% | -0.8523% | 0.7226% | -77.06% | -2.121% | -3.233% | -6.942% | -0.03102% | -0.03102% |  | -0.6409%
3081 | CEA | 2.238 | 1.6145 | 0.66223 | 0.54075 | 0.80498 | 0.80498 | 1.2593 | 0.17362 | 0.82151 | 0.38571 | 0.17157 | 2.0643 | 2.0643
| EPANET | 2.23 | 1.64 | 0.64 | 0.53 | 0.79 | 0.79 | 1.27 | 0.17 | 0.84 | 0.37 | 0.2 | 2.06 | 2.06
| Absolute Difference | -0.00795 | 0.02549 | -0.02223 | -0.01075 | -0.01498 | -0.01498 | 0.01065 | -0.00362 | 0.01849 | -0.01571 | 0.02843 | -0.00433 | -0.00433
| Relative Difference | -0.3565% | 1.554% | -3.473% | -2.028% | -1.896% | -1.896% | 0.8386% | -2.129% | 2.201% | -4.246% | 14.22% | -0.2102% | -0.2102%
8460 | CEA | 8.0547 | 4.9811 | 1.7157 | 1.9065 | 3.5126 | 3.5126 | 4.7979 | 0.25572 | 3.4476 | 1.4152 | 0.42629 | 8.3104 | 8.3104
| EPANET | 8.15 | 5.05 | 1.64 | 1.88 | 3.48 | 3.48 | 4.83 | 0.16 | 3.38 | 1.37 | 0.4 | 8.31 | 8.31
| Absolute Difference | 0.09528 | 0.06887 | -0.07571 | -0.02652 | -0.03256 | -0.03256 | 0.03212 | -0.09572 | -0.06756 | -0.04523 | -0.02629 | -0.00044 | -0.00044
| Relative Difference | 1.169% | 1.364% | -4.616% | -1.411% | -0.9356% | -0.9356% | 0.665% | -59.82% | -1.999% | -3.301% | -6.572% | -0.005295% | -0.005295% |  | -0.5759%
Network 2_1P
PLANT
Timestep |  | PIPE0 | PIPE1 | PIPE2 | PIPE3 | PIPE4 | PIPE5 | PIPE6 | PIPE7 | PIPE8 | PIPE9 | PIPE10 | PIPE11 | PIPE12 |  | PIPE0 | PIPE1 | PIPE2 | PIPE5
55 | CEA | 0.93604 | 2.9667 | 4.9974 | 17.4796 | 15.449 | 0.93604 | 14.3543 | 5.2409 | 2.0307 | 7.0828 | 5.2409 | 22.477 | 2.0307
| EPANET | 0.5 | 2.53 | 4.56 | 17.92 | 15.89 | 0.5 | 14.35 | 5.24 | 2.03 | 7.08 | 5.24 | 22.48 | 2.03
| Absolute Difference | -0.43604 | -0.43671 | -0.43738 | 0.44037 | 0.44104 | -0.43604 | -0.00433 | -0.00087 | -0.00067 | -0.00279 | -0.00087 | 0.00299 | -0.00067
| Relative Difference | -87.21% | -17.26% | -9.592% | 2.457% | 2.776% | -87.21% | -0.03017% | -0.0166% | -0.033% | -0.03941% | -0.0166% | 0.0133% | -0.033% |  | -1.94% | -1.943% | -1.946% | -1.94%
2959 | CEA | 0.20806 | 0.52594 | 0.84382 | 3.2919 | 2.9741 | 0.20806 | 2.8642 | 0.5817 | 0.31788 | 1.9647 | 0.5817 | 4.1357 | 0.31788
| EPANET | 0.14 | 0.45 | 0.77 | 3.36 | 3.05 | 0.14 | 2.86 | 0.58 | 0.32 | 1.96 | 0.58 | 4.14 | 0.32
| Absolute Difference | -0.06806 | -0.07594 | -0.07382 | 0.06807 | 0.07595 | -0.06806 | -0.00423 | -0.0017 | 0.00212 | -0.00465 | -0.0017 | 0.00425 | 0.00212
| Relative Difference | -48.61% | -16.88% | -9.587% | 2.026% | 2.49% | -48.61% | -0.1479% | -0.2931% | 0.6625% | -0.2372% | -0.2931% | 0.1027% | 0.6625% |  | -1.644% | -1.834% | -1.783% | -1.644%
7334 | CEA | 0.44559 | 1.2138 | 1.982 | 7.403 | 6.6348 | 0.44559 | 6.3122 | 1.215 | 0.76819 | 4.3291 | 1.215 | 9.385 | 0.76819
| EPANET | 0.29 | 1.06 | 1.83 | 7.55 | 6.79 | 0.29 | 6.31 | 1.21 | 0.77 | 4.33 | 1.21 | 9.38 | 0.77
| Absolute Difference | -0.15559 | -0.15378 | -0.15197 | 0.14698 | 0.15517 | -0.15559 | -0.00223 | -0.00497 | 0.00181 | 0.00093 | -0.00497 | -0.00499 | 0.00181
| Relative Difference | -53.65% | -14.51% | -8.304% | 1.947% | 2.285% | -53.65% | -0.03534% | -0.4107% | 0.2351% | 0.02148% | -0.4107% | -0.0532% | 0.2351% |  | -1.659% | -1.639% | -1.62% | -1.659%
Network 2_2P
[13 empty] | PLANT | PLANT
Timestep |  | PIPE0 | PIPE1 | PIPE2 | PIPE3 | PIPE4 | PIPE5 | PIPE6 | PIPE7 | PIPE8 | PIPE9 | PIPE10 | PIPE11 | PIPE12 | PIPE13 | PIPE5
83 | CEA | 1.8799 | 3.6552 | 3.6552 | 4.6667 | 2.8914 | 0.10463 | 1.2207 | 8.3218 | 6.7562 | 2.7864 | 8.3218 | 8.3218 | 8.3218 | 6.7562
| EPANET | 1.85 | 3.63 | 3.63 | 4.7 | 2.92 | 0.08 | 1.22 | 8.32 | 6.76 | 2.79 | 8.32 | 8.32 | 8.32 | 6.76
| Absolute Difference | -0.02991 | -0.02519 | -0.02519 | 0.03334 | 0.02862 | -0.02463 | -0.00073 | -0.00185 | 0.00384 | 0.00358 | -0.00185 | -0.00185 | -0.00185 | 0.00384
| Relative Difference | -1.617% | -0.6939% | -0.6939% | 0.7094% | 0.9801% | -30.79% | -0.05984% | -0.02224% | 0.0568% | 0.1283% | -0.02224% | -0.02224% | -0.00022236 | 0.00056805 | -0.148%
2751 | CEA | 0.53122 | 0.81776 | 0.81776 | 1.1342 | 0.84768 | 0.24468 | 0.80582 | 1.952 | 2.2702 | 0.48757 | 1.952 | 1.952 | 1.952 | 2.2702
| EPANET | 0.53 | 0.82 | 0.82 | 1.13 | 0.85 | 0.25 | 0.81 | 1.95 | 2.27 | 0.49 | 1.95 | 1.95 | 1.85 | 2.27
| Absolute Difference | -0.00122 | 0.00224 | 0.00224 | -0.00422 | 0.00232 | 0.00532 | 0.00418 | -0.00198 | -0.00023 | 0.00243 | -0.00198 | -0.00198 | -0.10198 | -0.00023
| Relative Difference | -0.2302% | 0.2732% | 0.2732% | -0.3735% | 0.2729% | 2.128% | 0.516% | -0.1015% | -0.01013% | 0.4959% | -0.1015% | -0.1015% | -0.055124 | -0.00010132
8285 | CEA | 1.2084 | 1.2084 | 1.2084 | 2.2516 | 2.2516 | 1.2084 | 3.4601 | 3.4601 | 5.3864 | 1.5337 | 3.4601 | 3.4601 | 3.4601 | 5.3864
| EPANET | 1.19 | 1.19 | 1.19 | 2.27 | 2.27 | 1.19 | 3.46 | 3.46 | 5.39 | 1.53 | 3.46 | 3.46 | 3.46 | 5.39
| Absolute Difference | -0.01843 | -0.01843 | -0.01843 | 0.01837 | 0.01837 | -0.01843 | -6e-05 | -6e-05 | 0.00363 | -0.00375 | -6e-05 | -6e-05 | -6e-05 | 0.00363
| Relative Difference | -1.549% | -1.549% | -1.549% | 0.8093% | 0.8093% | -1.549% | -0.001734% | -0.001734% | 0.06735% | -0.2451% | -0.001734% | -0.001734% | -1.7341e-05 | 0.00067347
Highest Deviation relative to total mass flow
| Relative Deviation | PIPE0: Network 1_1P; PIPE1: Network 1_2P; PIPE2: Network 2_1P; PIPE3: Network 2_2P
| Timestep #1 | PIPE0: 0.1789%; PIPE1: 0.4041%; PIPE2: 1.946%; PIPE3: 0.2004%
| Timestep #2 | PIPE0: 0.3582%; PIPE1: 0.6187%; PIPE2: 1.783%; PIPE3: 0.1111%
| Timestep #3 | PIPE0: 0.1995%; PIPE1: 0.4144%; PIPE2: 1.62%; PIPE3: 0.2655%