## Price Lines
Source | Voltage | Cross Section Area in mm2 | Price | Unit | Conversion | Price in SGD/m | SGD/m/mm2
Havells | 22 kV | 150 | 997 | INR/m (excl. tax) | 0.02835 | 28.265 | 0.18843
Havells | 22 kV | 185 | 1180 | INR/m (excl. tax) | 0.02835 | 33.453 | 0.18083
Havells | 22 kV | 240 | 1357 | INR/m (excl. tax) | 0.02835 | 38.471 | 0.1603
Havells | 22 kV | 300 | 1528 | INR/m (excl. tax) | 0.02835 | 43.3188 | 0.1444
Havells | 22 kV | 400 | 1808 | INR/m (excl. tax) | 0.02835 | 51.2568 | 0.12814
Havells | 22 kV | 500 | 2232 | INR/m (excl. tax) | 0.02835 | 63.2772 | 0.12655
Havells | 22 kV | 630 | 2648 | INR/m (excl. tax) | 0.02835 | 75.0708 | 0.11916
Havells | 22 kV | 800 | 3093 | INR/m (excl. tax) | 0.02835 | 87.6866 | 0.10961
Havells | 22 kV | 1000 | 3980 | INR/m (excl. tax) | 0.02835 | 112.833 | 0.11283
DENA | 0.4kV | 150 | 100 | EUR/m (incl. works, 3 phase) | 0.25 | 25 | 0.16667
DENA | 10-30kV | 185 | 140 | EUR/m (incl. works, 3 phase) | 0.25 | 35 | 0.18919
Willis | 12.47kV | 300 | 150 | USD/mile (incl. works, 3 phase, 1997) | 0.21972 | 32.9576 | 0.10986

## Price Transformers
Source | Voltage | Rated Load in kVA | Price | Unit | Conversion | Price in SGD | SGD/kVA | SGD/kVA incl works
Naderi Paper | ??? | 10000 | 200000 | USD (incl. works) | 0.68 | 136000 | 13.6 | 27.2
Willis | ??? | 50 | 750 | USD (1997) | 2.1216 | 1591.2 | 31.824 | 63.648
dena | MS | 61000 | 1200000 | EUR (incl. works) | 0.75 | 900000 | 14.7541 | 29.5082
dena | NS | 260 | 10000 | EUR (incl. works) | 0.75 | 7500 | 28.8462 | 57.6923
Servo | ??? | 25 | 45000 | INR | 0.019 | 855 | 34.2 | 68.4
Servo | ??? | 100 | 150000 | INR | 0.019 | 2850 | 28.5 | 57
Servo | ??? | 250 | 270000 | INR | 0.019 | 5130 | 20.52 | 41.04
Servo | ??? | 400 | 335000 | INR | 0.019 | 6365 | 15.9125 | 31.825
Servo | ??? | 500 | 450000 | INR | 0.019 | 8550 | 17.1 | 34.2
Servo | ??? | 100 | 695000 | INR | 0.019 | 13205 | 132.05 | 264.1
Servo | ??? | 1250 | 850000 | INR | 0.019 | 16150 | 12.92 | 25.84
Servo | ??? | 1500 | 1000000 | INR | 0.019 | 19000 | 12.6667 | 25.3333
Servo | ??? | 2000 | 1295000 | INR | 0.019 | 24605 | 12.3025 | 24.605
Nav | 11000/433 | 315 | 199000 | INR (excl. tax) | 0.02565 | 5104.35 | 16.2043 | 32.4086
Nav | 11000/433 | 400 | 224000 | INR (excl. tax) | 0.02565 | 5745.6 | 14.364 | 28.728
Nav | 11000/433 | 500 | 266000 | INR (excl. tax) | 0.02565 | 6822.9 | 13.6458 | 27.2916
Nav | 22000/433 | 500 | 285000 | INR (excl. tax) | 0.02565 | 7310.25 | 14.6205 | 29.241
Nav | 33000/433 | 500 | 313000 | INR (excl. tax) | 0.02565 | 8028.45 | 16.0569 | 32.1138
Nav | 11000/433 | 630 | 307000 | INR (excl. tax) | 0.02565 | 7874.55 | 12.4993 | 24.9986
Nav | 22000/433 | 630 | 324000 | INR (excl. tax) | 0.02565 | 8310.6 | 13.1914 | 26.3829
Nav | 33000/433 | 630 | 364000 | INR (excl. tax) | 0.02565 | 9336.6 | 14.82 | 29.64
Nav | 11000/433 | 800 | 402000 | INR (excl. tax) | 0.02565 | 10311.3 | 12.8891 | 25.7783
Nav | 22000/433 | 800 | 412000 | INR (excl. tax) | 0.02565 | 10567.8 | 13.2098 | 26.4195
Nav | 33000/433 | 800 | 424000 | INR (excl. tax) | 0.02565 | 10875.6 | 13.5945 | 27.189
Nav | 11000/433 | 1000 | 444000 | INR (excl. tax) | 0.02565 | 11388.6 | 11.3886 | 22.7772
Nav | 22000/433 | 1000 | 453000 | INR (excl. tax) | 0.02565 | 11619.45 | 11.6195 | 23.2389
Nav | 33000/433 | 1000 | 468500 | INR (excl. tax) | 0.02565 | 12017.025 | 12.017 | 24.0341
Nav | 11000/433 | 1250 | 524000 | INR (excl. tax) | 0.02565 | 13440.6 | 10.7525 | 21.505
Nav | 22000/433 | 1250 | 536500 | INR (excl. tax) | 0.02565 | 13761.225 | 11.009 | 22.018
Nav | 33000/433 | 1250 | 561500 | INR (excl. tax) | 0.02565 | 14402.475 | 11.522 | 23.044
Nav | 11000/433 | 1600 | 627000 | INR (excl. tax) | 0.02565 | 16082.55 | 10.0516 | 20.1032
Nav | 22000/433 | 1600 | 685000 | INR (excl. tax) | 0.02565 | 17570.25 | 10.9814 | 21.9628
Nav | 33000/433 | 1600 | 700000 | INR (excl. tax) | 0.02565 | 17955 | 11.2219 | 22.4438
Nav | 11000/433 | 2000 | 734500 | INR (excl. tax) | 0.02565 | 18839.925 | 9.42 | 18.8399
Nav | 22000/433 | 2000 | 811000 | INR (excl. tax) | 0.02565 | 20802.15 | 10.4011 | 20.8022
Nav | 33000/433 | 2000 | 867500 | INR (excl. tax) | 0.02565 | 22251.375 | 11.1257 | 22.2514
Nav | 11000/433 | 2500 | 885000 | INR (excl. tax) | 0.02565 | 22700.25 | 9.0801 | 18.1602
Nav | 22000/433 | 2500 | 993000 | INR (excl. tax) | 0.02565 | 25470.45 | 10.1882 | 20.3764
Nav | 33000/433 | 2500 | 1067000 | INR (excl. tax) | 0.02565 | 27368.55 | 10.9474 | 21.8948
Nav | 11000/433 | 3000 | 1148500 | INR (excl. tax) | 0.02565 | 29459.025 | 9.8197 | 19.6394
Nav | 22000/433 | 3000 | 1206000 | INR (excl. tax) | 0.02565 | 30933.9 | 10.3113 | 20.6226
Nav | 33000/433 | 3000 | 1220000 | INR (excl. tax) | 0.02565 | 31293 | 10.431 | 20.862
Nav | 11000/433 | 3150 | 1206000 | INR (excl. tax) | 0.02565 | 30933.9 | 9.8203 | 19.6406
Nav | 22000/433 | 3150 | 1265000 | INR (excl. tax) | 0.02565 | 32447.25 | 10.3007 | 20.6014
Nav | 33000/433 | 3150 | 1286000 | INR (excl. tax) | 0.02565 | 32985.9 | 10.4717 | 20.9434

## Tech Param Lines
|  |  | X = XL - Graigner |  | BC = 1 / XC - Graigner |  | XC = 1 / (ωC) | X = XL = ωL - Graigner
12.7/22 kV | Cable Cross Section | R | X | Z | Bsh | Smax | C | L | Y | G | B | Imax
Copper | mm2 | Ω/km | Ω/km | Ω/km | S/km | MVA | μF/km | mH/km | Ω/km | S/km | S/km | Amps
| 25 | R: 0.93; X = XL - Graigner Z: 0.93; X = XL = ωL - Graigner Y: 1.0753; X = XL = ωL - Graigner G: 1.0753; X = XL = ωL - Graigner B: 0
| 35 | R: 0.671; X = XL - Graigner Z: 0.671; X = XL = ωL - Graigner Y: 1.4903; X = XL = ωL - Graigner G: 1.4903; X = XL = ωL - Graigner B: 0
| 50 | 0.495 | 0.137 | 0.51361 |  |  |  | 0.43631 | 1.947 | 1.8765 | 0.51934
| 70 | 0.343 | 0.13 | 0.36681 |  |  |  | 0.41401 | 2.7262 | 2.5493 | 0.96619
| 95 | 0.247 | 0.124 | 0.27638 | 5.966e-05 | 10.0979 | 0.19 | 0.3949 | 3.6182 | 3.2336 | 1.6234 | 265
| 120 | 0.196 | 0.119 | 0.2293 | 6.28e-05 | 11.4315 | 0.2 | 0.37898 | 4.3612 | 3.7279 | 2.2633 | 300
| 150 | 0.159 | 0.115 | 0.19623 | 6.908e-05 | 12.5747 | 0.22 | 0.36624 | 5.0961 | 4.1292 | 2.9865 | 330
| 185 | 0.127 | 0.114 | 0.17066 | 7.536e-05 | 14.2894 | 0.24 | 0.36306 | 5.8596 | 4.3605 | 3.9142 | 375
| 240 | 0.0965 | 0.11 | 0.14633 | 8.164e-05 | 16.3852 | 0.26 | 0.35032 | 6.8339 | 4.5068 | 5.1372 | 430
| 300 | 0.0769 | 0.105 | 0.13015 | 9.42e-05 | 18.2905 | 0.3 | 0.33439 | 7.6835 | 4.5399 | 6.1989 | 480
| 400 | 0.0602 | 0.101 | 0.11758 | 0.00010362 | 20.5768 | 0.33 | 0.32166 | 8.5049 | 4.3544 | 7.3056 | 540
| 500 | 0.0468 | 0.099 | 0.1095 | 0.00011304 | 22.8631 | 0.36 | 0.31529 | 9.132 | 3.9028 | 8.256 | 600
| 630 | 0.0362 | 0.095 | 0.10166 | 0.0001256 | 25.1494 | 0.4 | 0.30255 | 9.8364 | 3.5025 | 9.1917 | 660
| 800 | 0.0283 | 0.092 | 0.096254 | 0.0001413 | 27.4357 | 0.45 | 0.29299 | 10.3891 | 3.0545 | 9.93 | 720
| 1000 | 0.0225 | 0.09 | 0.09277 | 0.00015386 | 28.9599 | 0.49 | 0.28662 | 10.7794 | 2.6144 | 10.4575 | 760
| Conductor Resistance (R) | X = XL = ωL - Graigner Y: Reference: http://www.prabhatcables.com/download/pdf-HT-XLPE.pdf
| Nominal Size of Conductor | R: Minimum no. of wires; X = XL - Graigner Z: Max. D.C. Resistance at 20° C; BC = 1 / XC - Graigner Smax: A.C. Resistance at 90° C
|  | Compacted Round |  | Plain Copper | Aluminium | Plain Copper | Aluminium
| Sq.mm | R: CU.; X = XL - Graigner X: ALU.; X = XL - Graigner Z: Ohm/Km; BC = 1 / XC - Graigner Bsh: Ohm/Km; BC = 1 / XC - Graigner Smax: Ohm/Km; XC = 1 / (ωC) C: Ohm/Km
| 25 | R: 6; X = XL - Graigner X: 6; X = XL - Graigner Z: 0.727; BC = 1 / XC - Graigner Bsh: 1.2; BC = 1 / XC - Graigner Smax: 0.93; XC = 1 / (ωC) C: 1.54
| 35 | R: 6; X = XL - Graigner X: 6; X = XL - Graigner Z: 0.524; BC = 1 / XC - Graigner Bsh: 0.868; BC = 1 / XC - Graigner Smax: 0.671; XC = 1 / (ωC) C: 1.11
| 50 | R: 6; X = XL - Graigner X: 6; X = XL - Graigner Z: 0.387; BC = 1 / XC - Graigner Bsh: 0.641; BC = 1 / XC - Graigner Smax: 0.495; XC = 1 / (ωC) C: 0.82
| 70 | R: 12; X = XL - Graigner X: 12; X = XL - Graigner Z: 0.268; BC = 1 / XC - Graigner Bsh: 0.443; BC = 1 / XC - Graigner Smax: 0.343; XC = 1 / (ωC) C: 0.567
| 95 | R: 15; X = XL - Graigner X: 15; X = XL - Graigner Z: 0.193; BC = 1 / XC - Graigner Bsh: 0.32; BC = 1 / XC - Graigner Smax: 0.247; XC = 1 / (ωC) C: 0.41
| 120 | R: 18; X = XL - Graigner X: 15; X = XL - Graigner Z: 0.153; BC = 1 / XC - Graigner Bsh: 0.253; BC = 1 / XC - Graigner Smax: 0.196; XC = 1 / (ωC) C: 0.324
| 150 | R: 18; X = XL - Graigner X: 15; X = XL - Graigner Z: 0.124; BC = 1 / XC - Graigner Bsh: 0.206; BC = 1 / XC - Graigner Smax: 0.159; XC = 1 / (ωC) C: 0.264
| 185 | R: 30; X = XL - Graigner X: 30; X = XL - Graigner Z: 0.0991; BC = 1 / XC - Graigner Bsh: 0.164; BC = 1 / XC - Graigner Smax: 0.127; XC = 1 / (ωC) C: 0.21
| 240 | R: 34; X = XL - Graigner X: 30; X = XL - Graigner Z: 0.0754; BC = 1 / XC - Graigner Bsh: 0.125; BC = 1 / XC - Graigner Smax: 0.0965; XC = 1 / (ωC) C: 0.16
| 300 | R: 34; X = XL - Graigner X: 30; X = XL - Graigner Z: 0.0601; BC = 1 / XC - Graigner Bsh: 0.1; BC = 1 / XC - Graigner Smax: 0.0769; XC = 1 / (ωC) C: 0.13
| 400 | R: 53; X = XL - Graigner X: 53; X = XL - Graigner Z: 0.047; BC = 1 / XC - Graigner Bsh: 0.0778; BC = 1 / XC - Graigner Smax: 0.0602; XC = 1 / (ωC) C: 0.1
| 500 | R: 53; X = XL - Graigner X: 53; X = XL - Graigner Z: 0.0366; BC = 1 / XC - Graigner Bsh: 0.0605; BC = 1 / XC - Graigner Smax: 0.0468; XC = 1 / (ωC) C: 0.0774
| 630 | R: 53; X = XL - Graigner X: 53; X = XL - Graigner Z: 0.0283; BC = 1 / XC - Graigner Bsh: 0.0469; BC = 1 / XC - Graigner Smax: 0.0362; XC = 1 / (ωC) C: 0.06
| 800 | R: 53; X = XL - Graigner X: 53; X = XL - Graigner Z: 0.0221; BC = 1 / XC - Graigner Bsh: 0.0367; BC = 1 / XC - Graigner Smax: 0.0283; XC = 1 / (ωC) C: 0.047
| 1000 | R: 53; X = XL - Graigner X: 53; X = XL - Graigner Z: 0.0176; BC = 1 / XC - Graigner Bsh: 0.0291; BC = 1 / XC - Graigner Smax: 0.0225; XC = 1 / (ωC) C: 0.0372
Short Circuit Rating for 1 sec duration (Ish) | bar: R to X = XL - Graigner X
| Nominal Size | R: XLPE Insulated
| Sq.mm | R: Copper; X = XL - Graigner X: Aluminium
| 25 | R: 3.6; X = XL - Graigner X: 2.4
| 35 | R: 5; X = XL - Graigner X: 3.3
| 50 | R: 7.1; X = XL - Graigner X: 4.7
| 70 | R: 10; X = XL - Graigner X: 6.6
| 95 | R: 13.6; X = XL - Graigner X: 9
| 120 | R: 17.1; X = XL - Graigner X: 11.3
| 150 | R: 21.4; X = XL - Graigner X: 14.2
| 185 | R: 26.4; X = XL - Graigner X: 17.5
| 240 | R: 34.3; X = XL - Graigner X: 22.6
| 300 | R: 42.9; X = XL - Graigner X: 28.3
| 400 | R: 57.1; X = XL - Graigner X: 37.7
| 500 | R: 71.4; X = XL - Graigner X: 47.2
| 630 | R: 90; X = XL - Graigner X: 59.4
| 800 | R: 114.3; X = XL - Graigner X: 75.5
| 1000 | R: 142.9; X = XL - Graigner X: 94.3
Approximate Capacitance for Single Core Cables (C) | bar: R to X = XL - Graigner Z
| Size | R: Voltage Grade (kV)
|  | 12.7/22 | 19/33 | 33/33
|  | μF/km | μF/km | μF/km
| 95 | R: 0.19; X = XL - Graigner X: 0.15; X = XL - Graigner Z: 0.14
| 120 | R: 0.2; X = XL - Graigner X: 0.16; X = XL - Graigner Z: 0.15
| 150 | R: 0.22; X = XL - Graigner X: 0.17; X = XL - Graigner Z: 0.16
| 185 | R: 0.24; X = XL - Graigner X: 0.18; X = XL - Graigner Z: 0.17
| 240 | R: 0.26; X = XL - Graigner X: 0.2; X = XL - Graigner Z: 0.19
| 300 | R: 0.3; X = XL - Graigner X: 0.23; X = XL - Graigner Z: 0.2
| 400 | R: 0.33; X = XL - Graigner X: 0.25; X = XL - Graigner Z: 0.23
| 500 | R: 0.36; X = XL - Graigner X: 0.27; X = XL - Graigner Z: 0.25
| 630 | R: 0.4; X = XL - Graigner X: 0.29; X = XL - Graigner Z: 0.28
| 800 | R: 0.45; X = XL - Graigner X: 0.33; X = XL - Graigner Z: 0.3
| 1000 | R: 0.49; X = XL - Graigner X: 0.35; X = XL - Graigner Z: 0.33
Approximate Reactance At 50 Hz For Single Core Cables (X) | bar: R to XC = 1 / (ωC) C
| Size | R: Voltage Grade(kV)
|  | 12.7/22 |  | 19/33 |  | 33/33
|  | Arm | Un-Arm | Arm | Un-Arm | Arm | Un-Arm
|  | Ohm/km | Ohm/km | Ohm/km | Ohm/km | Ohm/km | Ohm/km
| 50 | R: 0.137; X = XL - Graigner X: 0.13; X = XL - Graigner Z: 0.147; BC = 1 / XC - Graigner Bsh: 0.14
| 70 | R: 0.13; X = XL - Graigner X: 0.123; X = XL - Graigner Z: 0.141; BC = 1 / XC - Graigner Bsh: 0.133
| 95 | R: 0.124; X = XL - Graigner X: 0.116; X = XL - Graigner Z: 0.135; BC = 1 / XC - Graigner Bsh: 0.127; BC = 1 / XC - Graigner Smax: 0.143; XC = 1 / (ωC) C: 0.137
| 120 | R: 0.119; X = XL - Graigner X: 0.112; X = XL - Graigner Z: 0.13; BC = 1 / XC - Graigner Bsh: 0.122; BC = 1 / XC - Graigner Smax: 0.137; XC = 1 / (ωC) C: 0.131
| 150 | R: 0.115; X = XL - Graigner X: 0.107; X = XL - Graigner Z: 0.126; BC = 1 / XC - Graigner Bsh: 0.118; BC = 1 / XC - Graigner Smax: 0.134; XC = 1 / (ωC) C: 0.129
| 185 | R: 0.114; X = XL - Graigner X: 0.105; X = XL - Graigner Z: 0.124; BC = 1 / XC - Graigner Bsh: 0.115; BC = 1 / XC - Graigner Smax: 0.128; XC = 1 / (ωC) C: 0.122
| 240 | R: 0.11; X = XL - Graigner X: 0.101; X = XL - Graigner Z: 0.118; BC = 1 / XC - Graigner Bsh: 0.11; BC = 1 / XC - Graigner Smax: 0.124; XC = 1 / (ωC) C: 0.118
| 300 | R: 0.105; X = XL - Graigner X: 0.097; X = XL - Graigner Z: 0.112; BC = 1 / XC - Graigner Bsh: 0.105; BC = 1 / XC - Graigner Smax: 0.12; XC = 1 / (ωC) C: 0.114
| 400 | R: 0.101; X = XL - Graigner X: 0.093; X = XL - Graigner Z: 0.119; BC = 1 / XC - Graigner Bsh: 0.102; BC = 1 / XC - Graigner Smax: 0.115; XC = 1 / (ωC) C: 0.109
| 500 | R: 0.099; X = XL - Graigner X: 0.091; X = XL - Graigner Z: 0.105; BC = 1 / XC - Graigner Bsh: 0.099; BC = 1 / XC - Graigner Smax: 0.111; XC = 1 / (ωC) C: 0.106
| 630 | R: 0.095; X = XL - Graigner X: 0.089; X = XL - Graigner Z: 0.101; BC = 1 / XC - Graigner Bsh: 0.096; BC = 1 / XC - Graigner Smax: 0.108; XC = 1 / (ωC) C: 0.103
| 800 | R: 0.092; X = XL - Graigner X: 0.086; X = XL - Graigner Z: 0.097; BC = 1 / XC - Graigner Bsh: 0.092; BC = 1 / XC - Graigner Smax: 0.106; XC = 1 / (ωC) C: 0.099
| 1000 | R: 0.09; X = XL - Graigner X: 0.085; X = XL - Graigner Z: 0.096; BC = 1 / XC - Graigner Bsh: 0.09; BC = 1 / XC - Graigner Smax: 0.102; XC = 1 / (ωC) C: 0.096
“POLYCAB” SINGLE CORE COPPER CONDUCTOR, XLPE INSULATED, UNARMOURED & ARMOURED CABLES CONFORMING TO IS: 7098 PART-2/1985:
| Nominal Size of Conductor | R: Nominal Thickness of XLPE Insulation; X = XL - Graigner X: UNARMOURED CABLE; BC = 1 / XC - Graigner Smax: Min Thickness of Inner Sheath; XC = 1 / (ωC) C: ALUMINIUM STRIP ARMOURED CABLE; X = XL = ωL - Graigner B: ALUMINIUM ROUNDWIRE ARMOURED CABLE |  |  | CURRENT CARRYING CAPACITY |  |  | *Normal Delivery Length
|  |  | Nominal Thickness of PVC Outer Sheath | Approx. Overall Diameter of Cable | Approx. Weight of Cable |  | Nominal Dimesion of Strip | Minimum Thickness of PVC Outer Sheath | Approx. Overall Diameter of Cable | Approx. Weight of Cable | Nominal Dimesion of Round Wire | Minimum Thickness of PVC Outer Sheath | Approx. Overall Diameter of Cable | Approx. Weight of Cable | In Ground at 30° C. | In Duct at 30° C. | In Air at 40° C.
| Sq.mm. | mm | mm | mm | Kg/Km | mm | mm | mm | mm | Kg/Km | mm | mm | mm | Kg/Km | Amps. | Amps. | Amps. | Mtrs.
| 95 | 6 | 2.2 | 32 | 1650 | 0.4 | 0.8 | 1.56 | 33 | 1850 | 2 | 1.56 | 36 | 2050 | 265 | 230 | 345 | 500
| 120 | 6 | 2.2 | 34 | 1950 | 0.4 | 0.8 | 1.56 | 35 | 2150 | 2 | 1.56 | 37.5 | 2350 | 300 | 260 | 400 | 500
| 150 | 6 | 2.2 | 35 | 2250 | 0.4 | 0.8 | 1.56 | 36 | 2450 | 2 | 1.56 | 39 | 2700 | 330 | 290 | 450 | 500
| 185 | 6 | 2.2 | 37 | 2650 | 0.4 | 0.8 | 1.56 | 38 | 2850 | 2 | 1.72 | 41 | 3150 | 375 | 325 | 510 | 500
| 240 | 6 | 2.2 | 39 | 3200 | 0.4 | 0.8 | 1.56 | 40.5 | 3450 | 2 | 1.72 | 43 | 3750 | 430 | 370 | 600 | 500
| 300 | 6 | 2.2 | 41 | 3850 | 0.4 | 0.8 | 1.72 | 43 | 4100 | 2 | 1.72 | 45 | 4350 | 480 | 415 | 690 | 500
| 400 | 6 | 2.4 | 45 | 4900 | 0.5 | 0.8 | 1.88 | 47 | 5200 | 2 | 1.88 | 49 | 5500 | 540 | 465 | 790 | 500
| 500 | 6 | 2.6 | 48 | 5950 | 0.5 | 0.8 | 1.88 | 50 | 6200 | 2.5 | 2.04 | 53.5 | 6750 | 600 | 520 | 910 | 500
| 630 | 6 | 2.6 | 51.5 | 7200 | 0.5 | 0.8 | 2.04 | 54 | 7600 | 2.5 | 2.04 | 57 | 8050 | 660 | 570 | 1020 | 500
| 800 | 6 | 2.8 | 56 | 8950 | 0.6 | 0.8 | 2.04 | 58 | 9300 | 2.5 | 2.2 | 61 | 9900 | 720 | 620 | 1140 | 500
| 1000 | 6 | 3 | 61 | 11000 | 0.6 | 0.8 | 2.2 | 62.5 | 11350 | 2.5 | 2.36 | 66 | 12000 | 760 | 660 | 1240 | 500